## Version History
Version | Date | Author | Description
0.1 | 2026-06-18 | Keystone Controller Logic | Draft SS50K Mini PCS supplemental model generated from Sinexcel_Mini_PCS_ss40k.json.

## 50101-MiniPCS
Address Offset | Group Offset | Name | English Name | 中文名 | 数据来源（Mini PCS / Sinexcel） | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Notes
|  | miniPcsSupplemental | [5 empty] | group | [6 empty] | Mini PCS Supplemental Telemetry / Diagnostics
0 |  | ID | Model ID |  | 50101 |  |  | uint16 | 1 |  |  |  | M | S | Model ID
1 |  | L | Model Length |  |  | 130 |  | uint16 | 1 |  |  |  | M | S | Model Length
|  | Site information | [5 empty] | group
2 |  | siteID | Site ID |  | From controller/site configuration | Actual value |  | uint32 | 2 |  |  |  | M |  | Site ID
4 |  | reserved1 | Reserved |  | Reserved string |  |  | string | 6 |  | ASCII
|  | PCS information | [5 empty] | group
10 |  | SN | Device Serial number |  | Same PCS serial number used by existing 40101/SN | Actual value |  | string | 16 |  | ASCII |  |  | S | Serial Number | Common SS identity field; current template exports PCS SN through 40101.
26 |  | reserved2 | Reserved |  | Reserved string |  |  | string | 4 |  | ASCII
|  | Identity | [5 empty] | group
30 |  | pcsVersionModel | Pcs Version Model |  | HRUS@11; length=21; parser=STR16BE | Actual value |  | string | 21 |  |  |  |  | S | VersionModel | PCS firmware/model version string decoded from Mini RO register 11
|  | Status and faults | [5 empty] | group
51 |  | systemChargeStatusWord | System Charge Status Word |  | HRUS@33 | Actual value | 8 | bitfield16 | 1 | [5 empty] | SystemChgStatusMap
|  | Status | [5 empty] | group
52 |  | systemDetailStatusWord | System Detail Status Word |  | HRUS@35 | Actual value | 15 | bitfield16 | 1 | [5 empty] | SystemDetailStatusMap | Mini PCS detailed system status word from RO register 35
|  | Supplemental telemetry | [5 empty] | group
53 |  | totalStopReadback | Total Stop Readback |  | HRUS@1002 | Actual value |  | uint16 | 1 | [5 empty] | TotalStop
|  | Status and faults | [5 empty] | group
54 |  | clearFaultReadback | Clear Fault Readback |  | HRUS@1003 | Actual value |  | uint16 | 1 | [5 empty] | ClearFault
|  | Control readbacks | [5 empty] | group
55 |  | onOffGridSwitchReadback | On Off Grid Switch Readback |  | HRUS@1006 | Actual value |  | uint16 | 1 | [5 empty] | OnOffGridSwitch
56 |  | controlMode | Control Mode |  | HRUS@1211 | Actual value |  | uint16 | 1 | [5 empty] | ControlMode
|  | Control | [5 empty] | group
57 |  | energyDispatchMode | Energy Dispatch Mode |  | HRUS@1021 | Actual value |  | uint16 | 1 | [5 empty] | EnergyDispatchMode | Mini PCS energy dispatching mode from register 1021
|  | Control readbacks | [5 empty] | group
58 |  | activePowerControlMode | Active Power Control Mode |  | HRUS@1022 | Actual value |  | uint16 | 1 |  | W |  |  |  | ActivePowerControlMode
59 |  | reactivePowerControlMode | Reactive Power Control Mode |  | HRUS@1023 | Actual value |  | uint16 | 1 |  | W |  |  |  | ReactivePowerControlMode
60 |  | powerChangeMode | Power Change Mode |  | HRUS@1301 | Actual value |  | uint16 | 1 |  | W |  |  |  | PowerChangeMode
|  | Grid protection/config readbacks | [5 empty] | group
61 |  | dcBusVoltage | Dc Bus Voltage |  | HR@494 | Actual value |  | int16 | 1 |  | V |  |  |  | DCBusVoltage
|  | DC bus diagnostics | [5 empty] | group
62 |  | dcCurrent | Dc Current |  | HR@108 | Actual value |  | int16 | 1 |  | A |  |  |  | DCcurrent
63 |  | dcPower | Dc Power |  | Calculated from {'vBat': 'DCInputVoltage', 'iBat': 'DCcurrent'}: (vBat * iBat) / 1000 | Actual value |  | int32 | 2 |  | W |  |  |  | DCpower
|  | Identity | [5 empty] | group
65 |  | pvdcSerialNumber | Pvdc Serial Number |  | HRUS@34000; length=11; parser=STR16BE | Actual value |  | string | 11 |  |  |  |  | S | PVDCSerialNumber | PVDC module serial number decoded from Mini PVDC register 34000
76 |  | pvdcVersionModel | Pvdc Version Model |  | HRUS@34011; length=21; parser=STR16BE | Actual value |  | string | 21 |  |  |  |  | S | PVDCVersionModel | PVDC module firmware/model version string decoded from Mini PVDC register 34011
|  | PVDC diagnostics | [5 empty] | group
97 |  | pvdcStatusWord | Pvdc Status Word |  | HRUS@34032 | Actual value | 10 | bitfield16 | 1 | [5 empty] | PVDCStatusWord
98 |  | pvdcStringStatusWord | Pvdc String Status Word |  | HRUS@34033 | Actual value | 15 | bitfield16 | 1 | [5 empty] | PVDCStringStatusWord
99 |  | pvdcGeneratingStatusWord | Pvdc Generating Status Word |  | HRUS@34034 | Actual value | 3 | bitfield16 | 1 | [5 empty] | PVDCGeneratingStatusWord
|  | Faults | [5 empty] | group
100 |  | pvdcFaultWord40 | Pvdc Fault Word40 |  | HRUS@34040 | Actual value |  | bitfield16 | 1 | [5 empty] | PVDCFaultWord40 | Raw PVDC fault word 34040: EPO, calibration/sampling/flash/DSP abnormalities, and PV side DSP parameter mismatch bits.
101 |  | pvdcFaultWord41 | Pvdc Fault Word41 |  | HRUS@34041 | Actual value |  | bitfield16 | 1 | [5 empty] | PVDCFaultWord41 | Raw PVDC communication fault word 34041.
102 |  | pvdcFaultWord42 | Pvdc Fault Word42 |  | HRUS@34042 | Actual value |  | bitfield16 | 1 | [5 empty] | PVDCFaultWord42 | Raw PVDC fan and auxiliary power fault word 34042.
103 |  | pvdcFaultWord43 | Pvdc Fault Word43 |  | HRUS@34043 | Actual value |  | bitfield16 | 1 | [5 empty] | PVDCFaultWord43 | Raw PVDC over-temperature and thermal derating word 34043.
104 |  | pvdcFaultWord44 | Pvdc Fault Word44 |  | HRUS@34044 | Actual value |  | bitfield16 | 1 | [5 empty] | PVDCFaultWord44 | Raw PVDC sensor, SPD, frequent-start, and PID fault word 34044.
105 |  | pvdcFaultWord45 | Pvdc Fault Word45 |  | HRUS@34045 | Actual value |  | bitfield16 | 1 | [5 empty] | PVDCFaultWord45 | Raw PVDC over-current/current abnormal word 34045.
106 |  | pvdcFaultWord46 | Pvdc Fault Word46 |  | HRUS@34046 | Actual value |  | bitfield16 | 1 | [5 empty] | PVDCFaultWord46 | Raw PVDC PV-side voltage, reverse connection, overload, and current recharge word 34046.
107 |  | pvdcFaultWord47 | Pvdc Fault Word47 |  | HRUS@34047 | Actual value |  | bitfield16 | 1 | [5 empty] | PVDCFaultWord47 | Raw PVDC bus-side voltage, contactor, insulation, reverse connection, and leakage self-test word 34047.
108 |  | pvdcFaultWord48 | Pvdc Fault Word48 |  | HRUS@34048 | Actual value |  | bitfield16 | 1 | [5 empty] | PVDCFaultWord48 | Raw PVDC current-limit alarm word 34048.
|  | PVDC diagnostics | [5 empty] | group
109 |  | pvSideTotalCurrent | Pv Side Total Current |  | HR@34066 | Actual value |  | int16 | 1 | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | A |  |  |  | PVSideTotalCurrent
110 |  | pvExternalDcBusVoltage | Pv External Dc Bus Voltage |  | HR@34076 | Actual value |  | int16 | 1 | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | V |  |  |  | PVExternalDcBusVoltage
111 |  | pvInternalDcBusVoltage | Pv Internal Dc Bus Voltage |  | HR@34077 | Actual value |  | int16 | 1 | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | V |  |  |  | PVInternalDcBusVoltage
112 |  | pvBusSidePower | Pv Bus Side Power |  | HR@34078 | Actual value |  | int16 | 1 | exportMultiplier=1000 | W |  |  |  | PVBusSidePower
113 |  | pvBusSideCurrent | Pv Bus Side Current |  | HR@34079 | Actual value |  | int16 | 1 | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | A |  |  |  | PVBusSideCurrent
114 |  | pvModuleTemperature | Pv Module Temperature |  | HR@34081 | Actual value |  | int16 | 1 |  | deg C |  |  |  | PVModuleTemperature
|  | Faults | [5 empty] | group
115 |  | sinexcelStatusWord36 | Sinexcel Status Word36 |  | HRUS@36 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelStatusWord36 | Raw Sinexcel PCS status word 36. Includes grid-reconnect state and electrical/transformer room fan stop bits.
116 |  | sinexcelStatusWord37 | Sinexcel Status Word37 |  | HRUS@37 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelStatusWord37 | Raw Sinexcel PCS status word 37. Includes AC/DC galvanic-break-device closed status bits.
117 |  | sinexcelFaultWord106 | Sinexcel Fault Word106 |  | HRUS@106 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord106 | Raw Sinexcel PCS fault/alarm word 106
118 |  | sinexcelFaultWord107 | Sinexcel Fault Word107 |  | HRUS@107 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord107 | Raw Sinexcel PCS fault/alarm word 107
119 |  | sinexcelFaultWord108 | Sinexcel Fault Word108 |  | HRUS@108 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord108 | Raw Sinexcel PCS fault/alarm word 108
120 |  | sinexcelFaultWord109 | Sinexcel Fault Word109 |  | HRUS@109 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord109 | Raw Sinexcel PCS fault/alarm word 109
121 |  | sinexcelFaultWord110 | Sinexcel Fault Word110 |  | HRUS@110 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord110 | Raw Sinexcel PCS fault/alarm word 110
122 |  | sinexcelFaultWord112 | Sinexcel Fault Word112 |  | HRUS@112 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord112 | Raw Sinexcel PCS fault/alarm word 112
123 |  | sinexcelFaultWord113 | Sinexcel Fault Word113 |  | HRUS@113 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord113 | Raw Sinexcel PCS fault/alarm word 113
124 |  | sinexcelFaultWord114 | Sinexcel Fault Word114 |  | HRUS@114 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord114 | Raw Sinexcel PCS fault/alarm word 114
125 |  | sinexcelFaultWord115 | Sinexcel Fault Word115 |  | HRUS@115 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord115 | Raw Sinexcel PCS fault/alarm word 115
126 |  | sinexcelFaultWord118 | Sinexcel Fault Word118 |  | HRUS@118 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord118 | Raw Sinexcel PCS fault/alarm word 118
127 |  | sinexcelFaultWord119 | Sinexcel Fault Word119 |  | HRUS@119 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord119 | Raw Sinexcel PCS fault/alarm word 119
128 |  | sinexcelFaultWord120 | Sinexcel Fault Word120 |  | HRUS@120 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord120 | Raw Sinexcel PCS fault/alarm word 120
129 |  | sinexcelFaultWord121 | Sinexcel Fault Word121 |  | HRUS@121 | Actual value |  | bitfield16 | 1 | [5 empty] | SinexcelFaultWord121 | Raw Sinexcel PCS fault/alarm word 121

## 50101-BitDefinitions
Model ID | Name | Address Offset | Source Register | Bit | Bit Name | Value | Notes
50101 | systemChargeStatusWord | 51 | HRUS@33 | 0 | systemRunning | 1=active, 0=inactive
50101 | systemChargeStatusWord | 51 | HRUS@33 | 1 | systemStandby | 1=active, 0=inactive
50101 | systemChargeStatusWord | 51 | HRUS@33 | 2 | systemCharging | 1=active, 0=inactive
50101 | systemChargeStatusWord | 51 | HRUS@33 | 3 | systemDischarging | 1=active, 0=inactive
50101 | systemChargeStatusWord | 51 | HRUS@33 | 4 | systemFullyCharged | 1=active, 0=inactive
50101 | systemChargeStatusWord | 51 | HRUS@33 | 5 | systemTotallyDischarged | 1=active, 0=inactive
50101 | systemChargeStatusWord | 51 | HRUS@33 | 6 | systemConstantVoltageToppingCharge | 1=active, 0=inactive
50101 | systemChargeStatusWord | 51 | HRUS@33 | 7 | systemConstantVoltageFloatCharge | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 0 | requestUploadFault | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 1 | requestUploadEnergy | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 2 | initializingDsp | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 3 | droopActive | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 4 | syncActive | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 5 | deratingTemperature | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 6 | deratingBms | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 7 | deratingVoltage | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 8 | deratingFrequency | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 9 | dcDcSinglePhase | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 10 | selfAgingMode | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 11 | controlBoxAteMode | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 12 | cabinetAteMode | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 13 | dcBlackStartInProgress | 1=active, 0=inactive
50101 | systemDetailStatusWord | 52 | HRUS@35 | 14 | ffrActive | 1=active, 0=inactive
50101 | pvdcStatusWord | 97 | HRUS@34032 | 0 | pvdcFailed | 1=active, 0=inactive
50101 | pvdcStatusWord | 97 | HRUS@34032 | 1 | pvdcFault | 1=active, 0=inactive
50101 | pvdcStatusWord | 97 | HRUS@34032 | 2 | pvdcAlarm | 1=active, 0=inactive
50101 | pvdcStatusWord | 97 | HRUS@34032 | 3 | pvdcOnline | 1=active, 0=inactive
50101 | pvdcStatusWord | 97 | HRUS@34032 | 4 | pvdcBooting | 1=active, 0=inactive
50101 | pvdcStatusWord | 97 | HRUS@34032 | 5 | pvdcRunning | 1=active, 0=inactive
50101 | pvdcStatusWord | 97 | HRUS@34032 | 6 | pvdcDerating | 1=active, 0=inactive
50101 | pvdcStatusWord | 97 | HRUS@34032 | 7 | pvdcInitializingDsp | 1=active, 0=inactive
50101 | pvdcStatusWord | 97 | HRUS@34032 | 8 | pvdcRequestUploadFault | 1=active, 0=inactive
50101 | pvdcStatusWord | 97 | HRUS@34032 | 9 | pvdcRequestUploadEnergy | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 0 | pv1Running | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 1 | pv2Running | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 2 | pv3Running | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 3 | pv1Alarm | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 4 | pv2Alarm | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 5 | pv3Alarm | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 6 | pv1Fault | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 7 | pv2Fault | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 8 | pv3Fault | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 9 | pv1Failed | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 10 | pv2Failed | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 11 | pv3Failed | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 12 | pv1MpptApplying | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 13 | pv2MpptApplying | 1=active, 0=inactive
50101 | pvdcStringStatusWord | 98 | HRUS@34033 | 14 | pv3MpptApplying | 1=active, 0=inactive
50101 | pvdcGeneratingStatusWord | 99 | HRUS@34034 | 0 | pv1Generating | 1=active, 0=inactive
50101 | pvdcGeneratingStatusWord | 99 | HRUS@34034 | 1 | pv2Generating | 1=active, 0=inactive
50101 | pvdcGeneratingStatusWord | 99 | HRUS@34034 | 2 | pv3Generating | 1=active, 0=inactive
50101 | pvdcFaultWord40 | 100 | HRUS@34040 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw PVDC fault word 34040: EPO, calibration/sampling/flash/DSP abnormalities, and PV side DSP parameter mismatch bits.
50101 | pvdcFaultWord41 | 101 | HRUS@34041 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw PVDC communication fault word 34041.
50101 | pvdcFaultWord42 | 102 | HRUS@34042 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw PVDC fan and auxiliary power fault word 34042.
50101 | pvdcFaultWord43 | 103 | HRUS@34043 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw PVDC over-temperature and thermal derating word 34043.
50101 | pvdcFaultWord44 | 104 | HRUS@34044 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw PVDC sensor, SPD, frequent-start, and PID fault word 34044.
50101 | pvdcFaultWord45 | 105 | HRUS@34045 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw PVDC over-current/current abnormal word 34045.
50101 | pvdcFaultWord46 | 106 | HRUS@34046 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw PVDC PV-side voltage, reverse connection, overload, and current recharge word 34046.
50101 | pvdcFaultWord47 | 107 | HRUS@34047 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw PVDC bus-side voltage, contactor, insulation, reverse connection, and leakage self-test word 34047.
50101 | pvdcFaultWord48 | 108 | HRUS@34048 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw PVDC current-limit alarm word 34048.
50101 | sinexcelStatusWord36 | 115 | HRUS@36 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS status word 36. Includes grid-reconnect state and electrical/transformer room fan stop bits.
50101 | sinexcelStatusWord37 | 116 | HRUS@37 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS status word 37. Includes AC/DC galvanic-break-device closed status bits.
50101 | sinexcelFaultWord106 | 117 | HRUS@106 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 106
50101 | sinexcelFaultWord107 | 118 | HRUS@107 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 107
50101 | sinexcelFaultWord108 | 119 | HRUS@108 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 108
50101 | sinexcelFaultWord109 | 120 | HRUS@109 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 109
50101 | sinexcelFaultWord110 | 121 | HRUS@110 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 110
50101 | sinexcelFaultWord112 | 122 | HRUS@112 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 112
50101 | sinexcelFaultWord113 | 123 | HRUS@113 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 113
50101 | sinexcelFaultWord114 | 124 | HRUS@114 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 114
50101 | sinexcelFaultWord115 | 125 | HRUS@115 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 115
50101 | sinexcelFaultWord118 | 126 | HRUS@118 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 118
50101 | sinexcelFaultWord119 | 127 | HRUS@119 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 119
50101 | sinexcelFaultWord120 | 128 | HRUS@120 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 120
50101 | sinexcelFaultWord121 | 129 | HRUS@121 | 0..15 | Raw supplier bitfield | 1=active, 0=inactive | Raw Sinexcel PCS fault/alarm word 121

## Template Export View
Model ID | Model Index | Equipment | Tag ID | Export Name | Function | Modbus Address | Length | Parser | Poll Class | Scale | Export Multiplier | Category | Alarm | Supporting | Status / Bitfield | Description
50101 | 50 | PCS | VersionModel | pcsVersionModel | HRUS | 11 | 21 | STR16BE | startup |  |  | Identity | No | No |  | PCS firmware/model version string decoded from Mini RO register 11
50101 | 50 | PCS | SystemChgStatusMap | systemChargeStatusWord | HRUS | 33 |  |  | normal |  |  |  | No | No | bit 0: systemRunning; bit 1: systemStandby; bit 2: systemCharging; bit 3: systemDischarging; bit 4: systemFullyCharged; bit 5: systemTotallyDischarged; bit 6: systemConstantVoltageToppingCharge; bit 7: systemConstantVoltageFloatCharge
50101 | 50 | PCS | SystemDetailStatusMap | systemDetailStatusWord | HRUS | 35 |  |  | normal |  |  | Status | No | No | bit 0: requestUploadFault; bit 1: requestUploadEnergy; bit 2: initializingDsp; bit 3: droopActive; bit 4: syncActive; bit 5: deratingTemperature; bit 6: deratingBms; bit 7: deratingVoltage; bit 8: deratingFrequency; bit 9: dcDcSinglePhase; bit 10: selfAgingMode; bit 11: controlBoxAteMode; bit 12: cabinetAteMode; bit 13: dcBlackStartInProgress; bit 14: ffrActive | Mini PCS detailed system status word from RO register 35
50101 | 50 | PCS | TotalStop | totalStopReadback | HRUS | 1002 |  |  | manual |  |  |  | No | No
50101 | 50 | PCS | ClearFault | clearFaultReadback | HRUS | 1003 |  |  | manual |  |  |  | No | No
50101 | 50 | PCS | OnOffGridSwitch | onOffGridSwitchReadback | HRUS | 1006 |  |  | normal |  |  |  | No | No
50101 | 50 | PCS | ControlMode | controlMode | HRUS | 1211 |  |  | normal |  |  |  | No | No
50101 | 50 | PCS | EnergyDispatchMode | energyDispatchMode | HRUS | 1021 |  |  | normal |  |  | Control | No | No |  | Mini PCS energy dispatching mode from register 1021
50101 | 50 | PCS | ActivePowerControlMode | activePowerControlMode | HRUS | 1022 |  |  | normal |  |  |  | No | No
50101 | 50 | PCS | ReactivePowerControlMode | reactivePowerControlMode | HRUS | 1023 |  |  | normal |  |  |  | No | No
50101 | 50 | PCS | PowerChangeMode | powerChangeMode | HRUS | 1301 |  |  | normal |  |  |  | No | No
50101 | 50 | PCS | DCBusVoltage | dcBusVoltage | HR | 494 |  |  | normal |  |  |  | No | No
50101 | 50 | PCS | DCcurrent | dcCurrent | HR | 108 |  |  | normal |  |  |  | No | No
50101 | 50 | PCS | DCpower | dcPower |  |  |  |  | normal |  |  |  | No | No
50101 | 50 | PCS | PVDCSerialNumber | pvdcSerialNumber | HRUS | 34000 | 11 | STR16BE | startup |  |  | Identity | No | No |  | PVDC module serial number decoded from Mini PVDC register 34000
50101 | 50 | PCS | PVDCVersionModel | pvdcVersionModel | HRUS | 34011 | 21 | STR16BE | startup |  |  | Identity | No | No |  | PVDC module firmware/model version string decoded from Mini PVDC register 34011
50101 | 50 | PCS | PVDCStatusWord | pvdcStatusWord | HRUS | 34032 |  |  | normal |  |  |  | No | No | bit 0: pvdcFailed; bit 1: pvdcFault; bit 2: pvdcAlarm; bit 3: pvdcOnline; bit 4: pvdcBooting; bit 5: pvdcRunning; bit 6: pvdcDerating; bit 7: pvdcInitializingDsp; bit 8: pvdcRequestUploadFault; bit 9: pvdcRequestUploadEnergy
50101 | 50 | PCS | PVDCStringStatusWord | pvdcStringStatusWord | HRUS | 34033 |  |  | normal |  |  |  | No | No | bit 0: pv1Running; bit 1: pv2Running; bit 2: pv3Running; bit 3: pv1Alarm; bit 4: pv2Alarm; bit 5: pv3Alarm; bit 6: pv1Fault; bit 7: pv2Fault; bit 8: pv3Fault; bit 9: pv1Failed; bit 10: pv2Failed; bit 11: pv3Failed; bit 12: pv1MpptApplying; bit 13: pv2MpptApplying; bit 14: pv3MpptApplying
50101 | 50 | PCS | PVDCGeneratingStatusWord | pvdcGeneratingStatusWord | HRUS | 34034 |  |  | normal |  |  |  | No | No | bit 0: pv1Generating; bit 1: pv2Generating; bit 2: pv3Generating
50101 | 50 | PCS | PVDCFaultWord40 | pvdcFaultWord40 | HRUS | 34040 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw PVDC fault word 34040: EPO, calibration/sampling/flash/DSP abnormalities, and PV side DSP parameter mismatch bits.
50101 | 50 | PCS | PVDCFaultWord41 | pvdcFaultWord41 | HRUS | 34041 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw PVDC communication fault word 34041.
50101 | 50 | PCS | PVDCFaultWord42 | pvdcFaultWord42 | HRUS | 34042 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw PVDC fan and auxiliary power fault word 34042.
50101 | 50 | PCS | PVDCFaultWord43 | pvdcFaultWord43 | HRUS | 34043 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw PVDC over-temperature and thermal derating word 34043.
50101 | 50 | PCS | PVDCFaultWord44 | pvdcFaultWord44 | HRUS | 34044 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw PVDC sensor, SPD, frequent-start, and PID fault word 34044.
50101 | 50 | PCS | PVDCFaultWord45 | pvdcFaultWord45 | HRUS | 34045 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw PVDC over-current/current abnormal word 34045.
50101 | 50 | PCS | PVDCFaultWord46 | pvdcFaultWord46 | HRUS | 34046 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw PVDC PV-side voltage, reverse connection, overload, and current recharge word 34046.
50101 | 50 | PCS | PVDCFaultWord47 | pvdcFaultWord47 | HRUS | 34047 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw PVDC bus-side voltage, contactor, insulation, reverse connection, and leakage self-test word 34047.
50101 | 50 | PCS | PVDCFaultWord48 | pvdcFaultWord48 | HRUS | 34048 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw PVDC current-limit alarm word 34048.
50101 | 50 | PCS | PVSideTotalCurrent | pvSideTotalCurrent | HR | 34066 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
50101 | 50 | PCS | PVExternalDcBusVoltage | pvExternalDcBusVoltage | HR | 34076 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
50101 | 50 | PCS | PVInternalDcBusVoltage | pvInternalDcBusVoltage | HR | 34077 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
50101 | 50 | PCS | PVBusSidePower | pvBusSidePower | HR | 34078 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | 1000 |  | No | No
50101 | 50 | PCS | PVBusSideCurrent | pvBusSideCurrent | HR | 34079 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
50101 | 50 | PCS | PVModuleTemperature | pvModuleTemperature | HR | 34081 |  |  | normal |  |  |  | No | No
50101 | 50 | PCS | SinexcelStatusWord36 | sinexcelStatusWord36 | HRUS | 36 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS status word 36. Includes grid-reconnect state and electrical/transformer room fan stop bits.
50101 | 50 | PCS | SinexcelStatusWord37 | sinexcelStatusWord37 | HRUS | 37 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS status word 37. Includes AC/DC galvanic-break-device closed status bits.
50101 | 50 | PCS | SinexcelFaultWord106 | sinexcelFaultWord106 | HRUS | 106 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 106
50101 | 50 | PCS | SinexcelFaultWord107 | sinexcelFaultWord107 | HRUS | 107 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 107
50101 | 50 | PCS | SinexcelFaultWord108 | sinexcelFaultWord108 | HRUS | 108 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 108
50101 | 50 | PCS | SinexcelFaultWord109 | sinexcelFaultWord109 | HRUS | 109 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 109
50101 | 50 | PCS | SinexcelFaultWord110 | sinexcelFaultWord110 | HRUS | 110 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 110
50101 | 50 | PCS | SinexcelFaultWord112 | sinexcelFaultWord112 | HRUS | 112 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 112
50101 | 50 | PCS | SinexcelFaultWord113 | sinexcelFaultWord113 | HRUS | 113 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 113
50101 | 50 | PCS | SinexcelFaultWord114 | sinexcelFaultWord114 | HRUS | 114 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 114
50101 | 50 | PCS | SinexcelFaultWord115 | sinexcelFaultWord115 | HRUS | 115 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 115
50101 | 50 | PCS | SinexcelFaultWord118 | sinexcelFaultWord118 | HRUS | 118 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 118
50101 | 50 | PCS | SinexcelFaultWord119 | sinexcelFaultWord119 | HRUS | 119 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 119
50101 | 50 | PCS | SinexcelFaultWord120 | sinexcelFaultWord120 | HRUS | 120 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 120
50101 | 50 | PCS | SinexcelFaultWord121 | sinexcelFaultWord121 | HRUS | 121 |  |  | normal |  |  | Faults | Yes | Yes | bitfield | Raw Sinexcel PCS fault/alarm word 121

## Existing SS40K Coverage
Model ID | Model Index | Equipment | Tag ID | Export Name | Function | Modbus Address | Length | Parser | Poll Class | Scale | Export Multiplier | Category | Alarm | Supporting | Status / Bitfield | Description
40101 |  | PCS | SerialNumber | SN | HRUS | 0 | 11 | STR16BE | startup |  |  | Identity | No | No |  | PCS serial number decoded from register 0 as two-byte big-endian ASCII words
40101 |  | PCS | SystemStatusMap | invMode | HRUS | 32 |  |  | normal |  |  |  | No | No | bit 0: systemFault; bit 1: systemAlarm; bit 2: systemDerating; bit 3: systemBooting; bit 4: systemGridTied; bit 5: systemOffGrid; bit 6: systemPvHibernating; bit 7: systemPvGenerating; bit 8: systemPvMpptApplying; bit 9: systemFailed
40101 |  | PCS | ACBusTotalActivePower | W | HR | 168 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | 1000 |  | No | No
40101 |  | PCS | ACBusL1ActivePower | WL1 | HR | 169 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | 1000 |  | No | No
40101 |  | PCS | ACBusL2ActivePower | WL2 | HR | 170 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | 1000 |  | No | No
40101 |  | PCS | ACBusL3ActivePower | WL3 | HR | 171 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | 1000 |  | No | No
40101 |  | PCS | ACBusL1Current | AL1 | HR | 180 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | ACBusL2Current | AL2 | HR | 181 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | ACBusL3Current | AL3 | HR | 182 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | ACBusFrequency | Hz | HRUS | 183 |  |  | normal | mode=Linear; rawLow=0; rawHigh=100; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | ACBusL1L2Voltage | VL1L2 | HRUS | 184 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | ACBusL2L3Voltage | VL2L3 | HRUS | 185 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | ACBusL3L1Voltage | VL3L1 | HRUS | 186 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | ACBusL1NVoltage | VL1 | HRUS | 187 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | ACBusL2NVoltage | VL2 | HRUS | 188 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | ACBusL3NVoltage | VL3 | HRUS | 189 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40104 |  | PCS | GridRegulation | GridRegulation | HRUS | 2816 |  |  | normal |  |  |  | No | No
40104 |  | PCS | PermitService | PermitServiceStatus | HRUS | 1307 |  |  | normal |  |  |  | No | No
40104 |  | PCS | GridReconnectionDelay | ReconnectionDelayTime | HRUS | 1304 |  |  | normal |  |  |  | No | No
40104 |  | PCS | OverVoltRegion1Boundary | GridVoltLimit1Low | HRUS | 1341 |  |  | normal | mode=Linear; rawLow=0; rawHigh=1000; scaledLow=0; scaledHigh=1 |  |  | No | No
40104 |  | PCS | OverVoltRegion1TripTime | GridVoltLimit1High | HRUS | 1342 |  |  | normal |  |  |  | No | No
40104 |  | PCS | OverVoltRegion2Boundary | GridVoltLimit2Low | HRUS | 1343 |  |  | normal | mode=Linear; rawLow=0; rawHigh=1000; scaledLow=0; scaledHigh=1 |  |  | No | No
40104 |  | PCS | OverVoltRegion2TripTime | GridVoltLimit2High | HRUS | 1344 |  |  | normal |  |  |  | No | No
40104 |  | PCS | VoltWattStartV1 | VoltWattV1 | HRUS | 1411 |  |  | normal | mode=Linear; rawLow=0; rawHigh=1000; scaledLow=0; scaledHigh=1 |  |  | No | No
40104 |  | PCS | VoltWattEndV2 | VoltWattV2 | HRUS | 1412 |  |  | normal | mode=Linear; rawLow=0; rawHigh=1000; scaledLow=0; scaledHigh=1 |  |  | No | No
40104 |  | PCS | VoltWattStartP1 | VoltWattP1 | HRUS | 1413 |  |  | normal | mode=Linear; rawLow=0; rawHigh=1000; scaledLow=0; scaledHigh=1 |  |  | No | No
40104 |  | PCS | VoltWattEndP2 | VoltWattP2 | HRUS | 1414 |  |  | normal | mode=Linear; rawLow=0; rawHigh=1000; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | DCInputVoltage | vBat | HR | 493 |  |  | normal |  |  |  | No | No
40101 |  | PCS | PVSideTotalPower | pPvTotal | HR | 34053 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | 1000 |  | No | No
40101 |  | PCS | PV1SideTotalPower | pMppt1 | HR | 34054 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | 1000 |  | No | No
40101 |  | PCS | PV2SideTotalPower | pMppt2 | HR | 34055 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | 1000 |  | No | No
40101 |  | PCS | PV3SideTotalPower | pMppt3 | HR | 34056 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 | 1000 |  | No | No
40101 |  | PCS | PV1SideVoltage | vMppt1 | HR | 34063 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | PV2SideVoltage | vMppt2 | HR | 34064 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | PV3SideVoltage | vMppt3 | HR | 34065 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | PV1SideTotalCurrent | iMppt1 | HR | 34067 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | PV2SideTotalCurrent | iMppt2 | HR | 34068 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40101 |  | PCS | PV3SideTotalCurrent | iMppt3 | HR | 34069 |  |  | normal | mode=Linear; rawLow=0; rawHigh=10; scaledLow=0; scaledHigh=1 |  |  | No | No
40102 |  | PCS | PVGeneratedEnergy | ePvTot |  |  |  |  | slow |  | 1000 |  | No | No
40101 |  | PCS | ReactivePowerSetpoint | Var | HR | 1025 |  |  | manual |  |  |  | No | No
40103 |  | PCS | pcsWarning | pcsWarning |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 pcsWarning from Sinexcel PCS fault/alarm words
40103 |  | PCS | pcsFault | pcsFault |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 pcsFault from Sinexcel PCS fault/alarm words
40103 |  | PCS | pcsParaWarning | pcsParaWarning |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 pcsParaWarning from Sinexcel PCS fault/alarm words
40103 |  | PCS | PCSParaFault | PCSParaFault |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 PCSParaFault from Sinexcel PCS fault/alarm words
40103 |  | PCS | batWarning | batWarning |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 batWarning from Sinexcel PCS fault/alarm words
40103 |  | PCS | batFault | batFault |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 batFault from Sinexcel PCS fault/alarm words
40103 |  | PCS | gridWarning | gridWarning |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 gridWarning from Sinexcel PCS fault/alarm words
40103 |  | PCS | gridFault | gridFault |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 gridFault from Sinexcel PCS fault/alarm words
40103 |  | PCS | meterWarning | meterWarning |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 meterWarning from Sinexcel PCS fault/alarm words
40103 |  | PCS | bkupFault | bkupFault |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 bkupFault from Sinexcel PCS fault/alarm words
40103 |  | PCS | rsdEPOFault | rsdEPOFault |  |  |  |  | normal |  |  | Faults | Yes | No | bitfield | Calculated SS40K 40103 rsdEPOFault from Sinexcel PCS fault/alarm words